# MODEL 2900 Downflow

## Service Manual

#### IMPORTANT: Fill in pertinent information on page 3 for future reference.

Table of Contents

#### General Commercial Pre-Installation Check List.	4

Installation Instructions	4

#### 3200 Timer Setting Procedure	5

3210 Timer Settings	6

#### Regeneration Cycle Program Setting Procedure	7

3200 Timer Assembly	8

#### 3210 Timer Assembly	10

Environmental Power Head	12

#### Lower Environmental Power Head	14

Designer Power Head	16

#### Lower Designer Power Head	18

Control Valve Body	20

#### 1600 Brine System	22

1650 Brine System	23

#### 1700 Brine System	24

1710 Brine System	26

#### 2″ Meter Assembly	28

2″ Plastic Meter Assembly	29

#### 2300 Safety Brine Valve	30

2310 Safety Brine Valve	31

#### 2350 Safety Brine Valve	32

Service Valve Operator	33

#### Control Valve Side Mount Adapter	34

Service Assemblies	35

#### Service Instructions	36

Service Position	38

#### Backwash Position	39

Brine Position	40

#### Slow Rinse Position	41

Rapid Rinse	42

#### Brine Tank Fill Position	43

Flow Data & Injector Draw Rates	44

#### Environmental Backplate Line Drawing	46

Environmental Designer	47

#### System #4 - Typical Single Tank Installation With Optional Meter.	48

System #5 - Interlock - Typical Twin Tank Installation With Optional Meter Interlock

#### And No Hard Water Bypass	49

System #6 – Twin Series Regeneration	50

#### System #7 – Twin Alternator Installation	50

System #4-Single Valve Regeneration Immediate and Delayed Valve Wiring	51

#### System #4-With Remote Signal Start Valve Wiring	52

system #5-Interlocked Regeneration Valve Wiring	53

#### system #6-Series Regeneration Valve Wiring	54

system #7-Alternating Regeneration Valve Wiring	55

#### system #7-Alternating Regeneration Multi-Valve System Valve Wiring	56

IMPORTANT: The information, specifications and illustrations in this manual are based on the latest information available at the time of printing. The manufacturer reserves the right to make changes at any time without notice.

## Job Specification Sheet

- JOB NO.

- MODEL NO.

- WATER TEST

- CAPACITY PER UNIT 	MAX. 	PER REGENERATION

- MINERAL TANK SIZE   DIA. 	HEIGHT

- BRINE TANK SIZE & SALT SETTING PER REGENERATION:

- 2900 CONTROL VALVE SPECIFICATIONS

  - Type of Timer (see pages 18-21)

    - 7 day or 12 day

    - * 1,250 to 21,250 gallon meter or

      - 6,250 to 106,250 gallon meter

      - Other

    - Meter Wiring Package

- System #4 - 1 tank; 1 meter; immediate or delayed regeneration

- System #5 - 2 tanks; 2 meters; interlock

- System #6 - 2 tanks; 1 meter; series regeneration

- System #7 - 2 tanks; 1 meter; alternator

- Timer Program Settings (see pages 18 and 19)

  - Backwash

  - Brine & Slow Rinse

  - Rapid Rinse

  - Brine Tank Refill

- Drain Line Flow Controllergpm

min. min. min. min.

- Brine Line Flow Controller -

- Injector Size #

- A) Hard Water By-Pass

B) No Hard Water By-Pass

### Page 3

Printed in U.S.A.

## General Commercial Pre-Installation Check List

WATER PRESSURE: A minimum of 25 pounds of water pressure is required for regeneration valve to operate effectively.

ELECTRICAL FACILITIES: A continuous 110 volt, 60 Hertz current supply is required. Make certain the current supply is always hot and cannot be turned off with another switch.

EXISTING PLUMBING: Condition of existing plumbing should be free from lime and iron buildup. Piping that is built up heavily with lime and/or iron should be replaced. If piping is clogged with iron, a separate iron filter unit should be installed ahead of the water softener.

LOCATION OF SOFTENER AND DRAIN: The softener should be located close to a drain.

BY-PASS VALVES: Always provide for the installation of a by-pass valve.

CAUTION: Water pressure is not to exceed 120 p.s.i., water temperature is not to exceed 100° F, and the unit cannot be subjected to freezing conditions.

## Installation Instructions

- Place the softener tank where you want to install the unit making sure the unit is level and on a firm base. (Maximum 4 feet apart for twin units.)

- All plumbing should be done in accordance with local plumbing codes. The pipe size for the drain line should be the same size as the drain line flow control female connection. Water meters are to be installed on soft water outlets. Twin units with (1) one meter shall be installed on common soft water outlet of units.

- Solder joints near the drain must be done prior to connecting the Drain Line Flow Control fitting. Leave at least 6” between the DLFC and solder joints when soldering when the pipes are connected on the DLFC. Failure to do this could cause interior damage to the DLFC.

- Teflon tape is the only sealant to be used on the drain fitting. The drain from twin units may be run through a common line.

- Make sure that the floor is clean beneath the salt storage tank and that it is level.

- Place approximately 1″ of water above the grid plate (if used) in your salt tank. Salt may be placed in the unit at this time.

- On units with a by-pass, place in by-pass position. Turn on the main water supply. Open a cold soft water tap nearby and let run a few minutes or until the system is free from foreign material (usually solder) that may have resulted from the installation.

- Place the by-pass in service position.

- Manually index the softener control into “service” position and let water flow into the mineral tank. When water flow stops, open a cold water tap nearby and let run until air pressure is relieved.

- Electrical: All electrical connections must be connected according to codes. Use electrical conduit if applicable. Remote meter systems and Twin meter system wiring diagrams are on pages 26-29.

- Plug into power supply.

# MODEL 2900

## 3200 Timer Setting Procedure

#### How To Set Days On Which Water Conditioner Is To Regenerate:

Rotate the skipper wheel until the number “1” is at the red pointer. Set the days that regeneration is to occur by sliding tabs on the skipper wheel outward to expose trip fingers. Each tab is one day. Finger at red pointer is tonight. Moving clockwise from the red pointer, extend or retract fingers to obtain the desired regeneration schedule.

#### How To Set The Time Of Day:

Press and hold the red button in to disengage the drive gear.

Turn the large gear until the actual time of day is at the time of day pointer.

Release the red button to again engage the drive gear.

#### How To Manually Regenerate Your Water Conditioner At Any Time:

Turn the manual regeneration knob clockwise.

This slight movement of the manual regeneration knob engages the program wheel and starts the regeneration program.

The black center knob will make one revolution in the following approximately three hours and stop in the position shown in the drawing.

Even thought it takes three hours for this center knob to complete one revolution, the regeneration cycle of your unit might be set only one half of this time.

In any event, conditioned water may be drawn after rinse water stops flowing from the water conditioner drain line.

#### How to Adjust Regeneration Time:

  - Disconnect the power source.

  - Locate the three screws behind the manual regeneration knob by pushing the red button in and rotating the 24 hour dial until each screw appears in the cut out portion of the manual regeneration knob.

  - Loosen each screw slightly to release the pressure on the time plate from the 24 hour gear.

  - Locate the regeneration time pointer on the inside of the 24 hour dial in the cut out.

  - Turn the time plate so the desired regeneration time aligns next to the raised arrow.

SERVICE POSITION INDICATOR

RED TIME SET BUTTON

24 HR. GEAR

MANUAL REGENERATION KNOB

SKIPPER WHEEL, 12 DAY (SHOWS EVERY OTHER DAY REGENERATION)

Push the red button in and rotate the 24 hour dial. Tighten each of the three screws.

  - Push the red button and locate the pointer one more time to ensure the desired regeneration time is correct.

  - Reset the time of day and restore power to the unit.

3200 ADJUSTABLE REGENERATION TIMER

## 3210 Timer Settings

#### Typical Programming Procedure

Calculate the gallon capacity of the system, subtract the necessary reserve requirement and set the gallons available opposite the small white dot on the program wheel gear. Note, drawing shows 8,750 gallon setting. The capacity (gallons) arrow denotes remaining gallons exclusive of fixed reserve.

#### How To Set The Time Of Day:

Press and hold the red button in to disengage the drive gear.

Turn the large gear until the actual time of day is opposite the time of day pointer.

Release the red button to again engage the drive gear.

#### How To Manually Regenerate Your Water Conditioner At Any Time:

Turn the manual regeneration knob clockwise.

This slight movement of the manual regeneration knob engages the program wheel and starts the regeneration program.

The black center knob will make one revolution in the following approximately three hours and stop in the position shown in the drawing.

Even though it takes three hours for this center knob to complete one revolution, the regeneration cycle of your unit might be set for only one half of this time.

In any event, conditioned water may be drawn after rinse water stops flowing from the water conditioner drain line.

#### Immediate Regeneration Timers:

These timers do not have a 24 hour gear. Setting the gallons on the program wheel and manual regeneration procedure are the same as previous instructions.

* 24 HOUR GEAR

MANUAL REGENERATION KNOB

SERVICE POSITION INDICATOR

PROGRAM WHEEL

#### NOTE:

To set meter capacity rotate manual knob one - 360° revolution to set gallonage.

RED TIME SET BUTTON

WHITE DOT

GALLONS LABEL

* Immediate regeneration timers do not have 24 hour gear. No time of day can be set.

# MODEL 3200 & 3210 TIMER SERIES

## Regeneration Cycle Program Setting Procedure

(Brine Tank Refill Separate From Rapid Rinse)

How To Set The Regeneration Cycle Program:

The regeneration cycle program on your water conditioner has been factory preset, however, portions of the cycle or program may be lengthened or shortened in time to suit local conditions.

3200 & 3210 Series Timers (Figure to Right)

To expose cycle program wheel, grasp timer in upper left- hand corner and pull, releasing snap retainer and swinging timer to the right

To change the regeneration cycle program, the program wheel must be removed. Grasp program wheel and squeeze protruding lugs toward center, lift program wheel off timer. (Switch arms may require movement to facilitate removal.)

Return timer to closed position engaging snap retainer in back plate. Make certain all electrical wires locate above snap retainer post

Timer Setting Procedure for 3200 & 3210 Timer

How To Change The Length Of The Backwash Time:

The program wheel as shown in the drawing is in the service position. As you look at the numbered side of the program wheel, the group of pins starting at zero

BRINE & RINSE SECTION

(2 MIN. PER HOLE)

PIN STORAGE

BACKWASH SECTION

(2 MIN. PER PIN)

PROGRAM WHEEL FOR CONTROL OF REGENERATION CYCLE

RAPID RINSE SECTION (2 MIN. PER PIN)

BRINE TANK REFILL SECTION

(2 MIN.

PER HOLE)

determines the length of time your unit will backwash.

FOR EXAMPLE: If there are six pins in this section, the time of backwash will be 12 min. (2 min. per pin). To change the length of backwash time, add or remove pins as required. The number of pins times two equals the backwash time in minutes.

How To Change The Length Of Brine And Rinse Time:

The group of holes between the last pin in the backwash section and the second group of pins determines the length of time that your unit will brine and rinse (2 min. per hole.)

To change the length of brine and rinse time, move the rapid rinse group of pins to give more or fewer holes in the brine and rinse section. Number of holes times two equals brine and rinse time in minutes.

How To Change The Length Of Rapid Rinse:

The second group of pins on the program wheel determines the length of time that your water conditioner will rapid rinse. (2 min. per pin.)

To change the length of rapid rinse time, add or remove pins at the higher numbered end of this section as required. The number of pins times two equals the rapid rinse time in minutes.

How To Change The Length Of Brine Tank Refill Time:

The second group of holes in the program wheel determines the length of time that your water conditioner will refill the brine tank (2 min. per hole.)

To change the length of refill time, move the two pins at the end of the second group of holes as required.

The regeneration cycle is complete when the outer microswitch is tripped by the two pin set at end of the brine tank refill section.

The program wheel, however, will continue to rotate until the inner micro-switch drops into the notch on the program wheel.

## 3200 Timer Assembly

(See opposite page for parts list)

1	2

30

3

4

5

6

29

31	7

8

10	5

9	11

12

32	13

14

15

16

17	5

18

24	25	19

26

23	25

27

25	20

28

21

22

## 3200 Timer Assembly Parts List

#### Item No.	No. Req’d	Part No.	Description

1  . . . . . . . . . . . 1  . . . . . . . . . . . 13870	Timer Housing

2  . . . . . . . . . . . 1  . . . . . . . . . . . 13011	Cycle Actuator Arm

3  . . . . . . . . . . . 1  . . . . . . . . . . . 40096-24	24 Hour Gear Assembly, 12 Midnight

40096-02	24 Hour Gear Assembly, 2 a.m.

4  . . . . . . . . . . . 1  . . . . . . . . . . . 13886-01	Knob

5  . . . . . . . . . . . 5  . . . . . . . . . . . 13296	Screw - Timer Knob and Motor Mtg. Plate

6  . . . . . . . . . . . 1  . . . . . . . . . . . 11999	Button Decal

7  . . . . . . . . . . . 1  . . . . . . . . . . . 14381	Skipper Wheel Assembly - 12 Day

14860	Skipper Wheel Assembly - 7 Day

8  . . . . . . . . . . . 1  . . . . . . . . . . . 13014	Regeneration Pointer

9  . . . . . . . . . . . 1  . . . . . . . . . . . 14265	Spring Clip

10  . . . . . . . . . . 2  . . . . . . . . . . . 13311	Spring - Skipper Wheel Detent

11 . . . . . . . . . . 2  . . . . . . . . . . . 13300	Ball - 1/4 in. Dia. Skipper Wheel

12  . . . . . . . . . . 1  . . . . . . . . . . . 15424	Spring - Main Gear Detent

13  . . . . . . . . . . 1  . . . . . . . . . . . 13911	Main Drive Gear

14  . . . . . . . . . . 1  . . . . . . . . . . . 19210	Program Wheel

15  . . . . . . . . . . 21  . . . . . . . . . . 15493	Roll Pin

16  . . . . . . . . . . 1  . . . . . . . . . . . 13018	Idler Shaft

17  . . . . . . . . . . 1  . . . . . . . . . . . 13312	Spring - Idler

18  . . . . . . . . . . 1  . . . . . . . . . . . 13017	Idler Gear

19  . . . . . . . . . . 1  . . . . . . . . . . . 13164	Drive Gear

20  . . . . . . . . . . 1  . . . . . . . . . . . 13887	Motor Mounting Plate

21  . . . . . . . . . . 1  . . . . . . . . . . . 18743	Motor - 120V., 60 Hz.

19659	Motor - 24V., 60 Hz.

22  . . . . . . . . . . 2  . . . . . . . . . . . 13278	Screw - Motor Mounting

23  . . . . . . . . . . 3  . . . . . . . . . . . 11384	Screw - Timer Hinge & Ground Wire

24  . . . . . . . . . . 1  . . . . . . . . . . . 13881	Hinge Bracket

25  . . . . . . . . . . 3  . . . . . . . . . . . 14087	Insulator

26  . . . . . . . . . . 1  . . . . . . . . . . . 10896	Switch

27  . . . . . . . . . . 1  . . . . . . . . . . . 15320	Switch

28  . . . . . . . . . . 2  . . . . . . . . . . . 11413	Screw - Switch Mounting

29  . . . . . . . . . . 1  . . . . . . . . . . . 14007	Decal - Time of Day

30  . . . . . . . . . . 1  . . . . . . . . . . . 14045	Decal - Instructions

31  . . . . . . . . . . 1  . . . . . . . . . . . 13864	Skipper Wheel Ring

32  . . . . . . . . . . 1  . . . . . . . . . . . 15066	Ball 1/4 in. Dia. Main Gear

Not Shown. . . . 1  . . . . . . . . . . . 13902	Harness

Not Shown. . . . 2  . . . . . . . . . . . 12681	Wire Connector

Not Shown. . . . 1  . . . . . . . . . . . 15354-01	Ground Wire

## 3210 Timer Assembly

(See opposite page for parts list)

1

38

2

3

5

6

7

37

8

9	7

10	11

12

13

14

15

16

18

19

20

6

23

26

27

28

21

31	29

32

33	24

34	25

35

36

## 3210 Timer Assembly Parts List

#### Item No.	Quantity	Part No.	Description

1 . . . . . . . . . . . 1  . . . . . . . . . . . 13870-01	Timer Housing Assembly

2 . . . . . . . . . . . 1  . . . . . . . . . . . 13802	Cycle Actuator Gear

3 . . . . . . . . . . . 1  . . . . . . . . . . . 40096-24	24 Hour Gear Assembly, 12 Midnight

40096-02	24 Hour Gear Assembly, 2 A.M.

5 . . . . . . . . . . . 1  . . . . . . . . . . . 13886-01	Knob

6 . . . . . . . . . . . 4  . . . . . . . . . . . 13296	Screw - Timer Knob & Motor Plate Mtg.

7 . . . . . . . . . . . 2  . . . . . . . . . . . 11999	Button Decal

8 . . . . . . . . . . . 1 . . . . . . . . . . . 60405-50 . . . . . . . . . . . . . Program Wheel Assembly, 0-21,000

9 . . . . . . . . . . . 1  . . . . . . . . . . . 13806	Program Wheel Retainer

10  . . . . . . . . . . 1  . . . . . . . . . . . 13748	Screw - Program Wheel Mtg.

11  . . . . . . . . . . 1  . . . . . . . . . . . 14265	Spring Clip

12  . . . . . . . . . . 1  . . . . . . . . . . . 15424	Spring-Detent

13  . . . . . . . . . . 1  . . . . . . . . . . . 15066	Ball - 1/4 in. dia.

14  . . . . . . . . . . 1  . . . . . . . . . . . 13911	Main Drive Gear

15  . . . . . . . . . . 1  . . . . . . . . . . . 19210	Program Wheel Assembly

16  . . . . . . . . . . 21  . . . . . . . . . . 15493	Roll Pin

17	Not Assigned

18  . . . . . . . . . . 1  . . . . . . . . . . . 13018	Idler Shaft

19  . . . . . . . . . . 1  . . . . . . . . . . . 13312	Spring - Idler

20  . . . . . . . . . . 1  . . . . . . . . . . . 13017	Idler Gear

21  . . . . . . . . . . 1  . . . . . . . . . . . 13164	Drive Gear

23  . . . . . . . . . . 1  . . . . . . . . . . . 13887	Motor Mounting Plate

24  . . . . . . . . . . 1  . . . . . . . . . . . 18743	Motor - 110V., 60 Hz.

19659	Motor - 24V., 60 Hz.

25  . . . . . . . . . . 2  . . . . . . . . . . . 13278	Screw - Motor Mounting

26  . . . . . . . . . . 1  . . . . . . . . . . . 13830	Drive Pinion - Program Wheel

27  . . . . . . . . . . 1  . . . . . . . . . . . 13831	Clutch - Drive Pinion

28  . . . . . . . . . . 1  . . . . . . . . . . . 14276	Spring

29  . . . . . . . . . . 1  . . . . . . . . . . . 14253	Spring Retainer

30	Not Assigned

31  . . . . . . . . . . 3  . . . . . . . . . . . 11384	Screw - Timer Hinge & Ground Wire

32  . . . . . . . . . . 1  . . . . . . . . . . . 13881	Hinge Bracket

33  . . . . . . . . . . 3  . . . . . . . . . . . 14087	Insulator

34  . . . . . . . . . . 1  . . . . . . . . . . . 10896	Switch

35  . . . . . . . . . . 1  . . . . . . . . . . . 15320	Switch

36  . . . . . . . . . . 2  . . . . . . . . . . . 11413	Screw - Switch Mounting

37  . . . . . . . . . . 1  . . . . . . . . . . . 14007	Decal - Time of Day

38  . . . . . . . . . . 1  . . . . . . . . . . . 14045	Decal - Instructions

39  . . . . . . . . . . 1  . . . . . . . . . . . 13902	Harness - Not Shown

40  . . . . . . . . . . 2  . . . . . . . . . . . 12681	Wire Connector - Not Shown

41  . . . . . . . . . . 1  . . . . . . . . . . . 15354-01	Ground Wire - Not Shown

42  . . . . . . . . . . 1  . . . . . . . . . . . 15465	Caution Label - Not Shown

43  . . . . . . . . . . 1  . . . . . . . . . . . 14198	Capacity Label - Not Shown

## Environmental Power Head (See opposite page for parts list)

23 24

28

25 26 27

29	30

32

22	33

34

35

31

36

21

20	37

17

19

1	2

16

10

9

8

14

13

15 12

11	40	39

38

39

7

6

5

4

3	61501-29002

Page 12

## Environmental Power Head

Parts List

#### Item No.	Quantity	Part No.	Description

1 . . . . . . . . . . . 1  . . . . . . . . . . . 18697-15	Back Plate, Hinged, 2900

2 . . . . . . . . . . . - . . . . . . . . . . . . 3200 Clock Timer Assy . . 3200 Clock Timer Assy

2 . . . . . . . . . . . 1  . . . . . . . . . . . 3200 Meter Timer Assy . . 3200 Meter Timer Assy

3 . . . . . . . . . . . 1  . . . . . . . . . . . 40384	Motor, Drive, Shaded Pole, 115V, 60HZ, Fam

4 . . . . . . . . . . . 1  . . . . . . . . . . . 10774	Bracket, Motor

5 . . . . . . . . . . . 1  . . . . . . . . . . . 60160-10	CAM Drive Assy, STF, Black

6 . . . . . . . . . . . 1  . . . . . . . . . . . 17904	Bushing, Heyco 1/2, Heyco #2073

7 . . . . . . . . . . . 5 . . . . . . . . . . . 10872 . . . . . . . . . . . . . . . Screw, Hex Wsh, 8-32 X 17/64

8 . . . . . . . . . . . 3  . . . . . . . . . . . 10302	Insulator, Limit Switch

9 . . . . . . . . . . . 2  . . . . . . . . . . . 10218	Switch, Micro

10 . . . . . . . . . . 2 . . . . . . . . . . . 14923 . . . . . . . . . . . . . . . Screw, Pan Hd Mach, 4-40 X 1

11  . . . . . . . . . . 1  . . . . . . . . . . . 11826-02	Bracket, Motor, Aux Switch

12  . . . . . . . . . . 1  . . . . . . . . . . . 10896	Switch, Miniature

13 . . . . . . . . . . 2 . . . . . . . . . . . 11805 . . . . . . . . . . . . . . . Screw, Rd Hd, 4-40 X 5/8 Type 1

14  . . . . . . . . . . 1  . . . . . . . . . . . 12777-02	Cam, Shut-off Valve

15  . . . . . . . . . . 2  . . . . . . . . . . . 10338	Pin, Roll, 2900/3900

16  . . . . . . . . . . 1  . . . . . . . . . . . 10269	Nut, Jam, 3/4-16

17  . . . . . . . . . . 1  . . . . . . . . . . . 10712	Fitting, Brine Valve

18  . . . . . . . . . . 1  . . . . . . . . . . . 14822	Harness, 2900

19  . . . . . . . . . . 2  . . . . . . . . . . . 19691	Plug, .750 Dia. Hole, Flush

20  . . . . . . . . . . 1  . . . . . . . . . . . 15806	Hole Plug, (Heyco)

21  . . . . . . . . . . 1  . . . . . . . . . . . 19801	Plug, .190 Hole

22  . . . . . . . . . . 1  . . . . . . . . . . . 18693	Conduit, Interdrive

23  . . . . . . . . . . 1  . . . . . . . . . . . 18691-01	Fitting, Conduit

24  . . . . . . . . . . 1  . . . . . . . . . . . 18692	Washer, Sealing - 3/8"

25  . . . . . . . . . . 7  . . . . . . . . . . . 19800	Plug (Hole Size: Dia .140)

26 . . . . . . . . . . 4 . . . . . . . . . . . 10300 . . . . . . . . . . . . . . . Screw, Slot Hex Wsh, 8-18 X 3/8

27  . . . . . . . . . . 1  . . . . . . . . . . . 18691-02	Nut, Conduit Fitting,1/2IN

28  . . . . . . . . . . 1  . . . . . . . . . . . 40038-03	Label, Voltage, 120V

29  . . . . . . . . . . 1  . . . . . . . . . . . 17421	Hole Plug, (Heyco)

30  . . . . . . . . . . 1  . . . . . . . . . . . 60219-02	Cover Assy, Environmental,Black W/Clear Window

31  . . . . . . . . . . 1  . . . . . . . . . . . 19772	Bracket, Terminal Block

32  . . . . . . . . . . 1  . . . . . . . . . . . 40174	Terminal Block, Green/Yellow

33  . . . . . . . . . . 6  . . . . . . . . . . . 40184	Terminal Block, Segment, Gray

34  . . . . . . . . . . 1  . . . . . . . . . . . 41085	Endplate, Terminal Block, Gray

35  . . . . . . . . . . 2  . . . . . . . . . . . 15250	Label, Terminal Strip

36 . . . . . . . . . . 2 . . . . . . . . . . . 13296 . . . . . . . . . . . . . . . Screw, Hex Washer, 6-20 X 1/2

37  . . . . . . . . . . 1  . . . . . . . . . . . 40400	Harness, Drive, DesignR/Envirmtl

38  . . . . . . . . . . 1  . . . . . . . . . . . 40175-01	Wire, Ground, 7.5 Long

39 . . . . . . . . . . 1  . . . . . . . . . . . 40084-12	Power Cord, 12' US, Round, 120V

40  . . . . . . . . . . 1  . . . . . . . . . . . 13547-02	Strain Relief, Round Cord

41  . . . . . . . . . . - . . . . . . . . . . . . 17967 (Not Shown)	Fitting Assy, Liquid-Tight, Black

## Lower Environmental Power Head (See opposite page for parts list)

19	13	16

3	18

#### 5	14

4	17

#### 1	15

7	12

#### 6	22

8	11

#### 2	9

10	20

## Lower Environmental Power Head Parts List

#### Item No.	Quantity	Part No.	Description

1 . . . . . . . . . . . 1  . . . . . . . . . . . 18709	Back, Plate, Lower

2 . . . . . . . . . . . 2 . . . . . . . . . . . 11224 . . . . . . . . . . . . . . . Screw, Screw, Slotted Hex Head, 5/16 - 18 X 5/8

3 . . . . . . . . . . . 2  . . . . . . . . . . . 16346	Nut, Hex, Jam, 5/16-18, 18-8 S.S.

4 . . . . . . . . . . . 1  . . . . . . . . . . . 18692	Washer, Sealing - 3/8"

5 . . . . . . . . . . . 1  . . . . . . . . . . . 18691-01	Fitting, Conduit

6 . . . . . . . . . . . 1  . . . . . . . . . . . 18691-02	Nut, Conduit Fitting,1/2in

7 . . . . . . . . . . . 1  . . . . . . . . . . . 40387	Motor, Drive,115v,60hz,Sp, Fam 2

8 . . . . . . . . . . . 1  . . . . . . . . . . . 14769	Bracket, Motor,2900

9 . . . . . . . . . . . 1 . . . . . . . . . . . 40405	Harness, Lead, Sys#4, Designer

10  . . . . . . . . . . 1  . . . . . . . . . . . 10302	Insulator, Limit Switch

11  . . . . . . . . . . 1  . . . . . . . . . . . 10218	Switch, Micro

12 . . . . . . . . . . 2 . . . . . . . . . . . 19849 . . . . . . . . . . . . . . . Screw, Pan Hd, 4-40 X 5/8

13  . . . . . . . . . . 1  . . . . . . . . . . . 18746	Pin- Connecting Rod

14  . . . . . . . . . . 1  . . . . . . . . . . . 14775	Cam, Main Drive, 2900 Lower

15  . . . . . . . . . . 1  . . . . . . . . . . . 41022	Pin, Roll, 2900/3900

16  . . . . . . . . . . 1  . . . . . . . . . . . 14759	Link, Piston Rod

17  . . . . . . . . . . 1  . . . . . . . . . . . 10250	Ring, Retaining

18  . . . . . . . . . . 1  . . . . . . . . . . . 18725	Indicator, Service/Standby

19  . . . . . . . . . . 1  . . . . . . . . . . . 18726	Spacer, Indicator

20 . . . . . . . . . . 6 . . . . . . . . . . . 10872 . . . . . . . . . . . . . . . Screw, Hex Wsh,8-32 X 17/64

21  . . . . . . . . . . 6  . . . . . . . . . . . 14044 (Not Shown)	Tie, Cable, Heyco, Vnt#4-18

22  . . . . . . . . . . 1  . . . . . . . . . . . 60217-02	Cover Assy, 2900, Lower, Black, Environmental

## Designer Power Head

(See opposite page for parts list)

35

31

#### 21	27	28  29	30

26

#### 25

32

#### 24

23

#### 20	2

17

#### 11

22

#### 1

19

#### 10

9

#### 13

14	15	12

8

#### 7

6

#### 16  4	5

3

61501-29001

Page 16

## Designer Power Head

Parts List

#### Item No.	Quantity	Part No.	Description

1 . . . . . . . . . . . 1  . . . . . . . . . . . 40264	Backplate, SS/SVO, W/T-Screws, 2750,2850,2900

2 . . . . . . . . . . . 1  . . . . . . . . . . . 3200 Meter Timer Assy . . 3200 Meter Timer Assy

2 . . . . . . . . . . . - . . . . . . . . . . . . 3200 Clock Timer Assy . . 3200 Clock Timer Assy

3 . . . . . . . . . . . 1  . . . . . . . . . . . 11826-02	Bracket, Motor, Aux Switch

4 . . . . . . . . . . . 1  . . . . . . . . . . . 40384	Motor, Drive, Shaded Pole, 115V, 60HZ, Fam

5 . . . . . . . . . . . 1  . . . . . . . . . . . 10774	Bracket, Motor

6 . . . . . . . . . . . 1  . . . . . . . . . . . 60160-10	CAM Drive Assy, STF, Black

7 . . . . . . . . . . . 1  . . . . . . . . . . . 17904	Bushing, Heyco 1/2, Heyco #2073

8 . . . . . . . . . . . 5 . . . . . . . . . . . 10872 . . . . . . . . . . . . . . . Screw, Hex WSH, 8-32 X 17/64

9 . . . . . . . . . . . 3  . . . . . . . . . . . 10302	Insulator, Limit Switch

10  . . . . . . . . . . 2  . . . . . . . . . . . 10218	Switch, Micro

11 . . . . . . . . . . 2 . . . . . . . . . . . 14923 . . . . . . . . . . . . . . . Screw, Pan HD Mach, 4-40 X 1

12  . . . . . . . . . . 1  . . . . . . . . . . . 10896	Switch, Miniature

13 . . . . . . . . . . 2 . . . . . . . . . . . 11805 . . . . . . . . . . . . . . . Screw, RD HD, 4-40 X 5/8 Type 1

14  . . . . . . . . . . 2  . . . . . . . . . . . 12777-02	Cam, Shut-off Valve

15  . . . . . . . . . . 1  . . . . . . . . . . . 10338	Pin, Roll, 2900/3900

16  . . . . . . . . . . 1  . . . . . . . . . . . 10269	Nut, Jam, 3/4-16

17  . . . . . . . . . . 1  . . . . . . . . . . . 10712	Fitting, Brine Valve

18  . . . . . . . . . . 1  . . . . . . . . . . . 14822	Harness, 2900

19 . . . . . . . . . . 1  . . . . . . . . . . . 40174	Terminal Block, Green/Yellow

20  . . . . . . . . . . 6  . . . . . . . . . . . 40184	Terminal Block, Segment, Gray

21  . . . . . . . . . . 1  . . . . . . . . . . . 41085	Endplate, Terminal Block, Gray

22  . . . . . . . . . . 2  . . . . . . . . . . . 15250	Label, Terminal Strip

23 . . . . . . . . . . 2 . . . . . . . . . . . 13296 . . . . . . . . . . . . . . . Screw, Hex Washer, 6-20 X 1/2

24 . . . . . . . . . . 1  . . . . . . . . . . . 40084-12	Power Cord, 12'US, Round, 120V

25  . . . . . . . . . . 1  . . . . . . . . . . . 13547-02	Strain Relief, Round Cord

26  . . . . . . . . . . 1  . . . . . . . . . . . 15806	Hole Plug, (Heyco)

27  . . . . . . . . . . 1  . . . . . . . . . . . 17421	Hole Plug, (Heyco)

28 . . . . . . . . . . 1 . . . . . . . . . . . 13741 . . . . . . . . . . . . . . . Plug, 3/4", Knock-out, Heyco #2683

29 . . . . . . . . . . 2 . . . . . . . . . . . 10300 . . . . . . . . . . . . . . . Screw, Slot Hex Wsh, 8-18 X 3/8

30  . . . . . . . . . . 1  . . . . . . . . . . . 40038-03	Label, Voltage, 120V

31  . . . . . . . . . . 1  . . . . . . . . . . . 40400	Harness, Drive, Designr/Envirmtl

32  . . . . . . . . . . 1  . . . . . . . . . . . 40175-01	Wire, Ground, 7.5 Long

33  . . . . . . . . . . 1  . . . . . . . . . . . 17967 (Not Shown)	Fitting Assy, Liquid-Tight, Black (Meter)

34  . . . . . . . . . . 1  . . . . . . . . . . . 15158 (Not Shown)	TD Cable Guide (Meter)

35  . . . . . . . . . . 1  . . . . . . . . . . . 19291-020	Cover, Designer

## Lower Designer Power Head (See opposite page for parts list)

1

2

14

13

4

10

3

7

19

6

9

16

11

18

15

5	8

12

61501-29003

## Lower Designer Power Head Parts List

#### Item No.	Quantity	Part No.	Description

1 . . . . . . . . . . . 1  . . . . . . . . . . . 14770	Backplate, Lower 2900

2 . . . . . . . . . . . 1  . . . . . . . . . . . 14769	Bracket, Motor, 2900

3 . . . . . . . . . . . 2 . . . . . . . . . . . 11224 . . . . . . . . . . . . . . . SCREW Slotted Hex Head, 5/16 - 18 x 5/8

4 . . . . . . . . . . . 2  . . . . . . . . . . . 16346	Nut, Hex, Jam, 5/16-18, 18-8 S.S.

5 . . . . . . . . . . . 1 . . . . . . . . . . . 14924 . . . . . . . . . . . . . . . SR 7W-2

6 . . . . . . . . . . . 1  . . . . . . . . . . . 40387	Motor, Drive, 115V, 60HZ, SP, Fam 2

7 . . . . . . . . . . . 1  . . . . . . . . . . . 10250	Ring, Retaining

8 . . . . . . . . . . . 1  . . . . . . . . . . . 14759	Link, Piston Rod

9 . . . . . . . . . . . 1  . . . . . . . . . . . 14784	Bearing, Connecting Rod

10 . . . . . . . . . . 1  . . . . . . . . . . . 14775	Cam, Main Drive, 2900 Lower

11  . . . . . . . . . . 1  . . . . . . . . . . . 41022	Pin, Roll, 2900/3900

12 . . . . . . . . . . 2 . . . . . . . . . . . 19849 . . . . . . . . . . . . . . . Screw, Pan Hd, 4-40 X 5/8

13  . . . . . . . . . . 1  . . . . . . . . . . . 10218	Switch, Micro

14  . . . . . . . . . . 1  . . . . . . . . . . . 10302	Insulator, Limit Switch

15  . . . . . . . . . . 1  . . . . . . . . . . . 40402	Harness, Lead, Sys#4, Designer

16 . . . . . . . . . . 4 . . . . . . . . . . . 10872 . . . . . . . . . . . . . . . Screw, Hex Wsh, 8-32 X 17/64

17  . . . . . . . . . . 1  . . . . . . . . . . . 14044 (Not Shown)	Tie, Cable, Heyco, Vnt#4-18

18  . . . . . . . . . . 1  . . . . . . . . . . . 14800-02	Cover, Dust, Lower, 2900, Black

19  . . . . . . . . . . 2  . . . . . . . . . . . 19367	Screw, Designer Cover, Thumb

## Control Valve Body

(See opposite page for parts list)

1

8

5

2

4

28 27

26

7

9

10

6

3

13

12

11

25

24

23

20

1

16

15

18

14

17

19

21

22

61500-290019454

## Control Valve Body

Parts List

Item No.	Quantity	Part No.	Description

1 . . . . . . . . . . . 1 . . . . . . . . . . . 41428	Valve Body, 2900 CPI, Machined

1 . . . . . . . . . . . - . . . . . . . . . . . . 41428-xx	Valve Body, 2900 CPI, Machined, W/Soft Water Adapt

2 . . . . . . . . . . . 1  . . . . . . . . . . . 10757	Spacer, End

3 . . . . . . . . . . . 7  . . . . . . . . . . . 10545	Seal, Piston

4 . . . . . . . . . . . 6  . . . . . . . . . . . 11451	Spacer, 1 2 Hole

5 . . . . . . . . . . . 1  . . . . . . . . . . . 41425	Piston, 2900 CPI, Upper, D/F

5 . . . . . . . . . . . - . . . . . . . . . . . . 14451	Piston, 2750

6 . . . . . . . . . . . 1  . . . . . . . . . . . 14309	Retainer, Piston Rod

7 . . . . . . . . . . . 1  . . . . . . . . . . . 41424	Rod, Piston

8 . . . . . . . . . . . 1  . . . . . . . . . . . 41131	End Plug

9 . . . . . . . . . . . 1  . . . . . . . . . . . 10909	Ppin, Connecting Rod Spring

10 . . . . . . . . . . 1 . . . . . . . . . . . 10209 . . . . . . . . . . . . . . . Quad Ring,-010

11  . . . . . . . . . . 1  . . . . . . . . . . . 40078	O-ring, 28MM X 2MM

12  . . . . . . . . . . 4  . . . . . . . . . . . 11720	Seal, Piston, 2900/3150

13  . . . . . . . . . . 2  . . . . . . . . . . . 10369	Spacer, 2", 2900/3150

14  . . . . . . . . . . 1  . . . . . . . . . . . 14753	Spacer, 2900

15  . . . . . . . . . . 1  . . . . . . . . . . . 14757	Piston No HWBP 2900

16  . . . . . . . . . . 1  . . . . . . . . . . . 14818	Ring, Piston Rod, Snap

17  . . . . . . . . . . 1  . . . . . . . . . . . 14758	Piston Rod

18 . . . . . . . . . . 1 . . . . . . . . . . . 14922 . . . . . . . . . . . . . . . O-ring, -035

19 . . . . . . . . . . 1 . . . . . . . . . . . 14926 . . . . . . . . . . . . . . . Quad ring "O" ring-012

20  . . . . . . . . . . 1  . . . . . . . . . . . 14813	Connecting Link Pin

21  . . . . . . . . . . 1  . . . . . . . . . . . 13575  . . . . . . . . . . . . . . . O-ring, -240

22  . . . . . . . . . . 1  . . . . . . . . . . . 13577  . . . . . . . . . . . . . . . O-ring, -226

23  . . . . . . . . . . 1  . . . . . . . . . . . 14805	Gasket, Injector Body

24  . . . . . . . . . . 1  . . . . . . . . . . . 11893	Cap, Injector, SS

25 . . . . . . . . . . 2 . . . . . . . . . . . 15137 . . . . . . . . . . . . . . . Screw, Hex Washer Head, #10 - 24 X 3/8

26  . . . . . . . . . . - . . . . . . . . . . . . 41448	Adapter, Softwater Regen, 2900

27  . . . . . . . . . . - . . . . . . . . . . . . 16924  . . . . . . . . . . . . . . . O-ring, -018

28  . . . . . . . . . . - . . . . . . . . . . . . 19292  . . . . . . . . . . . . . . . O-ring, -020

1   2	3

15

4

14

5

13

6

12

4

11

5

10

9

7

3

5

8

7

8

24

16

1

1

19

20

21

22

23

4

#### Item No.	Quantity	Part No.	Description

1 . . . . . . . . . . . . 1 . . . . . . . . . . . . . 10328	90° Elbow - ¼ Pipe Thd. to 3/8″ Tube

2 . . . . . . . . . . . . 1 . . . . . . . . . . . . . 12767	Brine Line Screen

3 . . . . . . . . . . . . 2 . . . . . . . . . . . . . 10332	Insert Sleeve 3/8″ Tube)

4 . . . . . . . . . . . . 3 . . . . . . . . . . . . . 10329	Fitting Nut (3/8″ Tube)

5 . . . . . . . . . . . . 3 . . . . . . . . . . . . . 10330	Derlin Sleeve (3/8″ Tube)

6 . . . . . . . . . . . . 1 . . . . . . . . . . . . . 15221	Brine Valve Tube

7 . . . . . . . . . . . . 1 . . . . . . . . . . . . . 10250	Retaining Ring

8 . . . . . . . . . . . . 1 . . . . . . . . . . . . . 11749	Stem Guide

9 . . . . . . . . . . . . 1 . . . . . . . . . . . . . 10249	Brine Valve Spring

10 . . . . . . . . . . . . 1 . . . . . . . . . . . . . 12550	Quad Ring

11 . . . . . . . . . . . . 1 . . . . . . . . . . . . . 12748	Brine Valve Body

12 . . . . . . . . . . . . 1 . . . . . . . . . . . . . 12552	Brine Valve Stem

13 . . . . . . . . . . . . 1 . . . . . . . . . . . . . 12626	Brine Valve Seat

14 . . . . . . . . . . . . 1 . . . . . . . . . . . . . 11982	O-Ring

15 . . . . . . . . . . . . 1 . . . . . . . . . . . . . 60020-25	BLFC.25GPM

60020-50	BLFC .50 GPM

60020-100	BLFC 1.0 GPM

16. . . . . . . . . . . 2. . . . . . . . . . . . 10692. . . . . . . . . . . . . . . . Screw, Slotted, Indented Hex Head, #10 - 24 X 5/6

17. . . . . . . . . . . 1. . . . . . . . . . . . 11893	Cap, Injector, SS

18. . . . . . . . . . . 1. . . . . . . . . . . . 10229	Gasket, Injector Body

19. . . . . . . . . . . 1. . . . . . . . . . . . 10227	Screen, Injector

20. . . . . . . . . . . 1. . . . . . . . . . . . 10913	Nozzle, Injector, Std

21. . . . . . . . . . . 1. . . . . . . . . . . . 10914	Injector Throat, Std

22. . . . . . . . . . . 1. . . . . . . . . . . . 17776	Body, Injector, 1600

23. . . . . . . . . . . 1. . . . . . . . . . . . 16221	Disperser, Air

24. . . . . . . . . . . 1. . . . . . . . . . . . 14805	Gasket, Injector Body

Page 22

5

4

3

2

6

1

7

3

16

8

9

10

15

14

13

3

11

8

9

25

17

1

1

20

21

22

12	23

24

#### Item No.	Quantity	Part No.	Description 60011 Brine Valve Assembly, Includes Items 3-15 (Less BLFC 60010-)

1  . . . . . . . . . . . 1  . . . . . . . . . . . 10328	Elbow, 90 1/4 NPT x 3/8

2  . . . . . . . . . . . 1  . . . . . . . . . . . 12767	Screen, Brine Line

3  . . . . . . . . . . . 3  . . . . . . . . . . . 10332	nsert, 3/8

4  . . . . . . . . . . . 1  . . . . . . . . . . . 10330	Sleeve, 3/8 Nut Brine

5  . . . . . . . . . . . 1  . . . . . . . . . . . 10329	Tube Fitting, 3/8 Nut Brine

6  . . . . . . . . . . . 1  . . . . . . . . . . . 40027	Tube, Brine Valve

7  . . . . . . . . . . . 1  . . . . . . . . . . . 19625	Assy., GFN Nut

8  . . . . . . . . . . . 1  . . . . . . . . . . . 16924	O-Ring

9  . . . . . . . . . . . 1  . . . . . . . . . . . 12626	Seat, Brine Valve

10  . . . . . . . . . . 1  . . . . . . . . . . . 12552	Brine Valve Stem, 1600

11  . . . . . . . . . . 1  . . . . . . . . . . . 19625	Assy., GFN Nut

12  . . . . . . . . . . 1  . . . . . . . . . . . 17906	Guide, Brine Valve Stem

13  . . . . . . . . . . 1  . . . . . . . . . . . 10250	Retaining Ring

14  . . . . . . . . . . 1  . . . . . . . . . . . 10249	Spring, Brine Valve

15  . . . . . . . . . . 1  . . . . . . . . . . . 17884	Brine Valve Body Assy., Plastic

16  . . . . . . . . . . .  1 . . . . . . . . . . . . . 60020-25	BLFC.25GPM

60020-50	BLFC .50 GPM

60020-100	BLFC 1.0 GPM

17 . . . . . . . . . . 2 . . . . . . . . . . . 10692 . . . . . . . . . . . . . . . Screw, Slotted, Indented Hex Head, #10 - 24 X 5/6

18  . . . . . . . . . . 1  . . . . . . . . . . . 11893	Cap, Injector, SS

19  . . . . . . . . . . 1  . . . . . . . . . . . 10229	Gasket, Injector Body

20  . . . . . . . . . . 1  . . . . . . . . . . . 10227	Screen, Injector

21  . . . . . . . . . . 1  . . . . . . . . . . . 10913	Nozzle, Injector, Std

22  . . . . . . . . . . 1  . . . . . . . . . . . 10914	Injector Throat, Std

23  . . . . . . . . . . 1  . . . . . . . . . . . 17776	Body, Injector, 1600

24  . . . . . . . . . . 1  . . . . . . . . . . . 16221	Disperser, Air

25  . . . . . . . . . . 1  . . . . . . . . . . . 14805	Gasket, Injector Body

27

26

22	25

24

23

21

20

17	15	16

1

2

3	15

4

5

6

7

8

18

14	19

9

10	11

12 13

## 1700 Brine System Parts List

#### Item No.	Quantity	Part No.	Description

1 . . . . . . . . . . . 1	14792	End Plug

2 . . . . . . . . . . . 1  . . . . . . . . . . . 13201	O-Ring - End Plug

3 . . . . . . . . . . . 1  . . . . . . . . . . . 12085	Flow Washer 1.2 GPM

12086	Flow Washer 1.5 GPM

12087	Flow Washer 2.0 GPM

12088	Flow Washer 2.4 GPM

12089	Flow Washer 3.0 GPM

12090	Flow Washer 3.5 GPM

12091	Flow Washer 4.0 GPM

12092	Flow Washer 5.0 GPM

4 . . . . . . . . . . . 1  . . . . . . . . . . . 14785	Flow Control Retainer

5 . . . . . . . . . . . 2  . . . . . . . . . . . 14811	Piston Seals

6 . . . . . . . . . . . 1  . . . . . . . . . . . 14798	Spacer

7 . . . . . . . . . . . 1  . . . . . . . . . . . 14795	Brine Valve Piston

8 . . . . . . . . . . . 1  . . . . . . . . . . . 14797	Brine Valve Stem

9 . . . . . . . . . . . 1  . . . . . . . . . . . 14790	Brine Valve Body

10  . . . . . . . . . . 1  . . . . . . . . . . . 12550	Quad Ring - Brine Stem

11  . . . . . . . . . . 1  . . . . . . . . . . . 15310	Spring - Brine Valve

12  . . . . . . . . . . 1  . . . . . . . . . . . 10250	Retaining Ring

13  . . . . . . . . . . 1  . . . . . . . . . . . 15517	Stem Guide

14  . . . . . . . . . . 1  . . . . . . . . . . . 15415	Insert

15  . . . . . . . . . . 2  . . . . . . . . . . . 15414	Nut Ferrule 1/2″

16  . . . . . . . . . . 1  . . . . . . . . . . . 15413	Elbow

17  . . . . . . . . . . 1  . . . . . . . . . . . 15416	Brine Tube

18  . . . . . . . . . . 2  . . . . . . . . . . . 16123	Tube Nut 1/2″

19  . . . . . . . . . . 2  . . . . . . . . . . . 16124	Ferrule 1/2″

20  . . . . . . . . . . 1  . . . . . . . . . . . 16974	Fitting, Brass, Female 3/4″ x 3/4″ Slip - Not Shown

21  . . . . . . . . . . 1  . . . . . . . . . . . 11893	Injector Cover

22  . . . . . . . . . . 1  . . . . . . . . . . . 10229	Injector Cover Gasket

23  . . . . . . . . . . 1  . . . . . . . . . . . 17777	Injector Body

24  . . . . . . . . . . 1  . . . . . . . . . . . *14802	Injector Throat

25  . . . . . . . . . . 1  . . . . . . . . . . . *14801	Injector Nozzle

26  . . . . . . . . . . 1  . . . . . . . . . . . 14803	Injector Screen

27  . . . . . . . . . . 2  . . . . . . . . . . . 14804	Screw, Hex Head Mach, #10 - 24 X 2 3/4" 18-8 SS

*Injector Throat	*Injector Nozzle	Size Color 14802-03C  . . . . . 14801-03C  . . . . #3C	Yellow

14802-04C  . . . . . 14801-04C  . . . . #4C	Green

14802-05C  . . . . . 14801-05C  . . . . #5C	White

14802-06C  . . . . . 14801-06C  . . . . #6C	Red

14802-07C  . . . . . 14801-07C  . . . . #7C	Black

## 1710 Brine System

28

27

26

25

24

23

22

20

21

29

1

14

6

19

18

15

2

3

8

4

9

5

10

13

12

11

7

60604

## 1710 Brine System Parts List

#### Item No.	Quantity	Part No.	Description

1 . . . . . . . . . . . 1  . . . . . . . . . . . 41202	1700 Plastic Brine,Top

2 . . . . . . . . . . . 1  . . . . . . . . . . . 14785-01	Retainer, Flow Control

3 . . . . . . . . . . . - . . . . . . . . . . . . 14811	O-Ring, -210, 560CD

4 . . . . . . . . . . . 1  . . . . . . . . . . . 14798	Spacer, 2900

5 . . . . . . . . . . . 1  . . . . . . . . . . . 14795	Piston, Brine Valve

6 . . . . . . . . . . . 1  . . . . . . . . . . . 41203	Brine Valve Stem

7 . . . . . . . . . . . 1  . . . . . . . . . . . 41201	1700 Plastic Brine, Bottom

8 . . . . . . . . . . . 1 . . . . . . . . . . . 12550 . . . . . . . . . . . . . . . Ring, Quad -009

9 . . . . . . . . . . . 5  . . . . . . . . . . . 17908	Sleeve, Brine Valve Stem

10  . . . . . . . . . . 3  . . . . . . . . . . . 41547	O-Ring, 2mmx35mm

11  . . . . . . . . . . 2  . . . . . . . . . . . 15310	Spring, Brine Valve

12  . . . . . . . . . . 2  . . . . . . . . . . . 10250	Ring, Retaining

13  . . . . . . . . . . 1  . . . . . . . . . . . 17906	Guide, Brine Valve Stem

14  . . . . . . . . . . 2  . . . . . . . . . . . 14202-01	Screw, Hex Wsh Mach, 8-32 X 5/16"

15  . . . . . . . . . . 2  . . . . . . . . . . . 41056	Nut Assembly, 1/2"

16  . . . . . . . . . . 1  . . . . . . . . . . . 19151	Washer, Flow, 1.0 Gpm (not shown)

17  . . . . . . . . . . 1  . . . . . . . . . . . 41493-00	Label, Blfc, 1710 (not shown)

18  . . . . . . . . . . 1  . . . . . . . . . . . 16460	Tube, Brine, 2900

19  . . . . . . . . . . 1  . . . . . . . . . . . 15414	Nut, 2900, W/Sleeve

21  . . . . . . . . . . 1  . . . . . . . . . . . 19925	Gasket, Injector Body

22  . . . . . . . . . . 1  . . . . . . . . . . . 17777-03	Body, Injector, 1700

23  . . . . . . . . . . 1  . . . . . . . . . . . 14802-++C	Throat, Injector

24 . . . . . . . . . . 1 . . . . . . . . . . . 13771 . . . . . . . . . . . . . . . O-ring, -012

25  . . . . . . . . . . 1  . . . . . . . . . . . 14801-++C	Nozzle, Injector

26  . . . . . . . . . . 1  . . . . . . . . . . . 10229	Gasket, Injector Body

27  . . . . . . . . . . 1  . . . . . . . . . . . 10228	Cap, Injector

28  . . . . . . . . . . 2  . . . . . . . . . . . 14804	Screw, Hex Head Mach, #10 - 24 X 2 3/4" 18-8 SS

29  . . . . . . . . . . 1  . . . . . . . . . . . 15413	Fitting, Elbow, Male, 1/2T X 3/8NPT

## 2″ Meter Assembly

7B

12

11

10

9

1

8

7A

#### 6

5

#### 3

2

#### Item No.	Quantity	Part No.	Description

1 . . . . . . . . . . . 1	14456	Meter Body

2 . . . . . . . . . . . 1. . . . . . . . . . . . 15532	Impeller Shaft Retainer

3 . . . . . . . . . . . 1. . . . . . . . . . . . 15432	Impeller Shaft

4	Not Assigned

5 . . . . . . . . . . . 1. . . . . . . . . . . . 15374	Impeller

6 . . . . . . . . . . . 1. . . . . . . . . . . . 13847	O-Ring - Meter Cover

7A  . . . . . . . . . . 1. . . . . . . . . . . . 15218	Meter Cover Assembly (Standard)

7B  . . . . . . . . . . 1. . . . . . . . . . . . 15237	Meter Cover Assembly (Extended Range)

8 . . . . . . . . . . . 4. . . . . . . . . . . . 12112	Screw - Meter Cover

9 . . . . . . . . . . . 1. . . . . . . . . . . . 14679	O-Ring - Quick Connect

10. . . . . . . . . . . 1. . . . . . . . . . . . 14568	Nipple - Quick Connect

11. . . . . . . . . . . 1. . . . . . . . . . . . 14680	Flow Straightener

12. . . . . . . . . . . 1. . . . . . . . . . . . 14569	Nut - Quick Connect

## 2″ Plastic Meter Assembly

8

7

6

5

3

2

11

4

9

1

9

10

12

13

13

Item No.	Quantity	Part No.	Description

1 . . . . . . . . . . . . 1 . . . . . . . . . . . . 17689	Body, Meter, 2″ Plastic

2 . . . . . . . . . . . . 1 . . . . . . . . . . . . 15532	Shaft, Impeller Seat

3 . . . . . . . . . . . . 1 . . . . . . . . . . . . 15432	Shaft, Impeller

4 . . . . . . . . . . . . 1 . . . . . . . . . . . . 60620	Meter Assembly, 2″ (Standard Range)

. . . . . . . . . . . . 1 . . . . . . . . . . . . 60621	Meter Assembly, 2″ (Extended Range)

. . . . . . . . . . . . . . . . . . . . . . . . . 60625	Meter Assembly, 2″ (Electronic)

5 . . . . . . . . . . . . 1 . . . . . . . . . . . . 15374	Impeller Assembly, 2″ Meter

6 . . . . . . . . . . . . 1 . . . . . . . . . . . . 13847	O-Ring, -137, Meter

7 . . . . . . . . . . . . 1 . . . . . . . . . . . . 14038	Meter Cap Assembly (Standard Range)

1 . . . . . . . . . . . . 15150	Meter Cap Assembly (Extended Range)

1 . . . . . . . . . . . . 14716	Meter Cap Assembly (Electronic)

8 . . . . . . . . . . . . 4 . . . . . . . . . . . . 12473 . . . . . . . . . . . . . . . . .Screw, Hex Washer, 10-24 x 5/8

9 . . . . . . . . . . . . 2 . . . . . . . . . . . . 40666	Seal, Face, 2″, Plastic

10A . . . . . . . . . . 1 . . . . . . . . . . . . 17987-001	Fitting, Nipple, 2″, Plastic, NPT, Machined

10B . . . . . . . . . . 1 . . . . . . . . . . . . 17987-101	Fitting, Nipple, 2″, Plastic, BSP, Machined

11A . . . . . . . . . . 1 . . . . . . . . . . . . 17987-000	Fitting, Nipple, 2″, Plastic, NPT

11B . . . . . . . . . . 1 . . . . . . . . . . . . 17987-100	Fitting, Nipple, 2″, Plastic, BSP

12 . . . . . . . . . . . 1 . . . . . . . . . . . . 14680	Flow Straightener

13 . . . . . . . . . . . 2 . . . . . . . . . . . . 17988	Nut, 2″ Meter

| Item | Quantity | Part Number | Description |
| --- | --- | --- | --- |
| 1 | 1 | 60027-FFA | 2300 safety brine valve, fitting facing arm |
|  |  | 60027-FFS | 2300 safety brine valve, fitting facing stud |
| 2 | 1 | 60028-30 | float assembly blue/white |
|  |  | 60026-30SAN | float assembly green/green, hot water |
| 3 | 1 | 60002 | #500 air check |
|  |  | 60003 | #500 air check, hot water |

2310 Safety Brine Valve

| Item | Quantity | Part Number | Description |
| --- | --- | --- | --- |
| 1 | 1 | 60014 | 2310 safety brine valve |
| 2 | 1 | 60068 | 2310 float assembly |
|  |  | 60026-30 | float assembly red/white (float fill) |
| 3 | 1 | 60002 | #500 air check |

| Item | Quantity | Part Number | Description |
| --- | --- | --- | --- |
| 1 | 1 | 60038 | 2350 safety brine valve |
| 1A | 1 | 61024 | 2350 actuator assembly |
| 2 3 | 1 1 | 60026-30 60076-30SAN 60009-00 | float assembly red/white float assembly green/green (hot water) #900 air check |
|  | 1 | 60009-01 | #900 air check hot water |
| Not Shown 4 |  | 18603 | 2350 fittings for 1700 brine system |
| 5 |  | 18602 | #900 fittings for 1700 brine system |

# MODEL 2900

## Service Valve Operator

10	9	8

13

13

8

12

10

9

10

9

8

11

14a

12

10

9

8

14b

7

6

8

15

10

9

5	4

3	2

1

#### PARTS LIST

Item No.	Quantity	Part No.	Description

1 . . . . . . . . . . . 1. . . . . . . . . . . . 11749	Guide, Brine Valve Stem

2 . . . . . . . . . . . 1. . . . . . . . . . . . 10250	Retaining Ring

3 . . . . . . . . . . . 1. . . . . . . . . . . . 10249	Spring, Brine Valve

4 . . . . . . . . . . . 1. . . . . . . . . . . . 12550	Quad Ring

5 . . . . . . . . . . . 1. . . . . . . . . . . . 10785	Service Actuator Assembly - .25 gpm

6 . . . . . . . . . . . 1. . . . . . . . . . . . 12552	Brine Valve Stem, 1600

7 . . . . . . . . . . . 1. . . . . . . . . . . . 12626	Seat, Brine Valve

8 . . . . . . . . . . . 5. . . . . . . . . . . . 10332	Insert,

9 . . . . . . . . . . . 5. . . . . . . . . . . . 10330. . . . . . . . . . . . . . . . Sleeve, 3/8″ Delrin

10. . . . . . . . . . . 5. . . . . . . . . . . . 10329. . . . . . . . . . . . . . . . Nut, 3/8″ Brass

11. . . . . . . . . . . 1. . . . . . . . . . . . 10328	Elbow, 90° 1/4″ NPT x 3/8″

12. . . . . . . . . . . 2. . . . . . . . . . . . 12897	Tube

13. . . . . . . . . . . 2. . . . . . . . . . . . 16730. . . . . . . . . . . . . . . . Connector, Male 1/8″ NPT to 3/8″ T

14a. . . . . . . . . . 1. . . . . . . . . . . . 12472	Cam Assy. Tri stack, After Rapid Rinse

14b . . . . . . . . . 1. . . . . . . . . . . . 15770	Cam Assy. Tri stack, After Brine Tank Fill

15. . . . . . . . . . . 1. . . . . . . . . . . . 12114	Bracket, Motor Outboard

Page 33

Printed in U.S.A.

## Control Valve

Side Mount Adapter

7

#### Item No.	Quantity	Part No.	Description

1 . . . . . . . . . . . 1  . . . . . . . . . . . 40316	Adaptor, Side Mount

2 . . . . . . . . . . . 1  . . . . . . . . . . . 40372  . . . . . . . . . . . . . . . O-Ring - 142

3 . . . . . . . . . . . 1  . . . . . . . . . . . 40368  . . . . . . . . . . . . . . . O-Ring - 160

4 . . . . . . . . . . . 1  . . . . . . . . . . . 40310	Base, Rotating

5 . . . . . . . . . . . 7  . . . . . . . . . . . 40375	Washer

6 . . . . . . . . . . . 7  . . . . . . . . . . . 19768	Screw

7 . . . . . . . . . . . 1  . . . . . . . . . . . 61415	Assembly

# MODEL 2900

## Service Assemblies

| ADAPTERS |  | METERS |  |
| --- | --- | --- | --- |
| 61525 | Treated Water Regen Adapter Assembly | 60393 | 2” Meter brass standard range |
| 61415 | Sidemount Adaper Assembly | 60394 | 2” Meter brass extended range |
| 61415NP | Sidemount Adaper Assembly, Nickel Plated | 60616 | 2” Meter brass electronic |
| 61415-20 | Sidemount Adaper Assembly, BSP/Metric | 60620 | 2” Meter plastic standard range |
| 61415-20NP | Sidemount Adaper Assembly, BSP/Metric, Nickel Plated | 60621 | 2” Meter plastic Extended range |
|  |  | 60625 | 2” Meter plastic electronic |
| AIR CHECKS |  | 15474-02 | 1 ½” low flow sleeve only |
| 60002 | #500 Air Check |  |  |
| 60003 | #500 Air Check Hot Water | PISTON ASSEMBLIES |  |
| 60009 | # 900 Commercial Air Check | 61540 | Top piston |
| 60009-01 | # 900 Commercial Air Check Hot Water | 61540-01 | Top piston, Hot Water |
|  |  | 61550 | Lower piston, Hard Water By-Pass |
| AUXILARY MICRO SWITCH 61550-01 Lower piston, By-Pass, Treated Water Regen |  |  |  |
| 60320-02 | 3200 Series Timer | 61550-02 | Lower piston, By-Pass, Treated Water Regen, Hot Water |
| 60320-11 | Lower Drive (2nd Switch) | 61550-03 | Lower Piston, By-Pass, Hot Water |
| 60230-08 | Lower Drive (3rd Switch) | 61555 | Lower Piston, No By-Pass |
|  |  | 61555-01 | Lower Piston, No By-Pass, Treated Water Regen, Hot Water |
| BRINE LINE FLOW (BLFC) 61555-02 Lower Piston, No By-Pass, Treated Water Regen |  |  |  |
| 60020-00 | Model 1600, blank | 61555-03 | Lower Piston, No By-Pass, Hot Water |
| 60020-25 | Model 1600 with .25 gpm flow control |  |  |
| 60020-50 Model 1600 with .50 gpm flow control PROGRAM WHEEL ASSEMBLIES |  |  |  |
| 60020-100 | Model 1600 with 1.0 gpm flow control | 60405-20 | 1 ½” Std. Range ( 0 - 10,000 ) |
| 60010-00 | Model 1650, blank | 60405-50 | 2” Std. Range ( 0 - 21,000 ) |
| 60010-25 | Model 1650 with .25 gpm flow control | 60405-60 | 2” Ext. Range ( 0 - 100,000 ) |
| 60010-50 | Model 1650 with .50 gpm flow control | 60405-70 | 1 ½” Ext. Range ( 0 - 50,000 ) |
| 60010-100 | Model 1650 with 1.0 gpm flow control |  |  |
| SAFETY BRINE VALVES |  |  |  |
| BRINE VALVES |  | 60014 | Model 2310 plastic safety brine valve |
| 60011 | Model 1650 brine valve assy. | 60038 | Model 2350 Safety Brine Valve |
| 60029 | Model 1600 brine valve assy. | 60026-30 | Float Assy. (red/white) |
| 60029HW | Model 1600 Hot Water brine valve assy. | 60026-30SAN | San float assy. (Hot Water) |
| 60034-_ _ | Model 1700 brine valve assy.( specify flow control 1.0 - 5.0 ) | 60027-FFA | Model 2300 safety brine valve |
| 60604-_ _ | Model 1710 brine valve assy.( specify flow control 1.0 - 5.0 ) | 60027-FFS | Model 2300 Safety brine valve |
|  |  | 60028-30 | Float Assy. (blue/white) |
| COVERS |  | 60068-30 | Float Assy. 2310 |
| 60217-_ _ | Environmental lower cover |  |  |
| 60219-_ _ | Environmental | SALES AND SERVICE AIDS |  |
| 60232-_ _ | Designer 2 piece | 16864 -01 | Spec sheet |
| 60232-110 | Designer 1 piece ( only available in black ) | 15238 | Service manual |
| 60239-_ _ | Designer Lower cover | 41717 | Product line Catalog |
| DRIAN LINE FLOW CONTROLS SEAL & SPACER KITS |  |  |  |
| 60366-_ _ | 1" FNPT x ¾” FNPT ( specify flow control .6 - 7.0) | 61530 | Upper kit |
| 60701-_ _ | 1” FNPT x 1” FNPT ( specify flow control 8.0 - 25.0 ) | 61530-01 | Upper kit, Hot Water |
| 60702-_ _ | 1” FNPT x 1” MNPT ( specify flow control 8.0 - 25.0 ) | 60128 | Lower kit |
| 60708-_ _ | 1” FNPT x ¾” FNPT ( specify flow control 8.0 - 25.0 ) | 60128-01 | Lower kit, Hot Water |
| 60721-_ _ | 1" FNPT x 1” FNPT ( specify flow control .6 - 7.0) |  |  |
| SERVICE EQUIPMENT CAM ASSEMBLY 11098 Seal & Spacer stuffer tool upper |  |  |  |
| 60160-00 | Separate time fill drive cam ( Black ) | 12682 | Spacer puller tool lower |
| 60160-20 | Lower drive (Designer) | 12683 | Seal & Spacer stuffer tool lower |
| 60160-22 | Lower drive (Environmental) | 13061 | Spacer puller tool upper |
|  |  | 16174 | Silicone, 2 oz. Tube |
| 24 HOUR GEAR ASSEMBLY |  | 60460 | Meter Checker Std. Range |
| 19205 |  | 60461 | Meter Checker Ext. Range |
| 60519-02 | Model 3200 timer 2 times regeneration | 16586-8 | Silicone, 8 lb. pail |
| 60519-03 | Model 3200 timer 3 times regeneration |  |  |
| 60519-04 Model 3200 timer 4 times regeneration SERVICE VALVE OPERATOR ASSEMBLY ( SVO ) |  |  |  |
| 60519-06 | Model 3200 timer 6 times regeneration | 60150 | SVO (Old Style) |
|  |  | 60150-01 | SVO (New Style) |
| INJECTOR ASSEMBLIES COMPLETE 60483-_ _ _ 1700 - ½” brine (specify size of injector) SKIPPER WHEEL ASEMBLIES |  |  |  |
| 60480-_ _ | 1600 - 3/8” brine (specify size of injector) | 14860 | 3200 Timer 12 day |
| 60481-_ _ | 1600 Brass - 3/8” brine ( specify size of injector) | 14381 | 3200 Timer 7 day |

### Page 35

Printed in U.S.A.

## Service Instructions

| PROBLEM | CAUSE | CORRECTION |
| --- | --- | --- |
| - Softener Fails To Regenerate. - Hard Water. - Unit Used Too Much Salt - Loss Of Water Pressure. - Loss of Mineral Through Drain Line. - Iron In Conditioned Water. | - Electrical Service To Unit Has Been Interrupted. - Timer Is Defective. - Power Failure. - By-Pass Valve is Open. - No Salt in Brine Tank - Injector Screen Plugged. - Insufficient Water Flowing Into Brine Tank - Hot Water Tank Hardness. - Leak At Distributor Tube. - Internal Valve Leak - Service Adapter Did Not Return To Service. - Improper Salt Setting. - Excessive Water in Brine Tank - Iron Buildup In Line To Water Con- ditioner. - Iron Buildup in Water Conditioner. - Inlet of Control Plugged Due to Foreign Material Broken Loose From Pipes By Recent Work Done On Plumbing System. - Air In Water System. - Improperly Sized Drain Line Flow Control. A. Fouled Mineral Bed. | - Assure Permanent Electrical Ser- vice (Check Fuse, Plug, Pull Chain or Switch). - Replace Timer. - Reset Time of Day. - Close By-Pass Valve. - Add Salt To Brine Tank and Main- tain Salt Level Above Water Level. - Clean Injector Screen. - Check Brine Tank Fill Time And Clean Brine Line Flow Control If Plugged. - Repeated Flushings Of The Hot Water Tank is Required. - Make Sure Distributor Tube Is Not Cracked. Check O-Ring And Tube Pilot. - Replace Seals and Spacers And/ Or Piston. - Check Drive Motor And Switch. - Check Salt Usage and Salt Set- ting. - See Problem No. 7. - Clean Line To Water Conditioner. - Clean Control and Add Mineral Cleaner to Mineral Bed. Increased Frequency of Regeneration. - Remove Piston and Clean Control. - Assure That Well System Has Proper Air Eliminator Control. Check For Dry Well Condition. - Check For Proper Drain Rate. A. Check Backwash, Brine Draw And Brine Tank Fill. Increase Fre- quency of Regeneration. Increase Backwash Time. |

Service Instructions (Cont’d.)

| PROBLEM | CAUSE | CORRECTION |
| --- | --- | --- |
| - Excessive Water In Brine Tank. - Softener Fails To Draw Brine. - Control Cycles Continuously. - Drain Flows Continuously. | - Plugged Drain Line Flow Control. - Plugged Injector System. - Timer Not Cycling. - Foreign Material In Brine Valve. - Foreign Material In Brine Line Flow Control. - Drain Line Flow Control Is Plugged. - Injector Is Plugged. - Injector Screen Plugged. - Line Pressure Is Too Low. - Internal Control Leak - Service Adapter Did Not Cycle. A. Misadjusted, Broken or Shorted Switch. - Valve Is Not Programming Cor- rectly. - Foreign Material In Control. - Internal Control Leak | - Clean Flow Control. - Clean Injector and Screen. - Replace Timer. - Replace Brine Valve Seat And Clean Valve. - Clean Brine Line Flow Control. - Clean Drain Line Flow Control. - Clean Injector. - Clean Screen. - Increase Line Pressure To 20 P.S.I. - Change Seals, Spacers and Piston Assembly. - Check Drive Motor And Switches. A. Determine If Switch or Timer Is Faulty and Replace It or Replace Complete Power Head. - Check Timer Program and Posi- tioning of Control. Replace Power Head Assembly If Not Positioning Properly. - Remove Power Head Assembly And Inspect Bore. Remove Foreign Material and Check Control In Var- ious Regeneration Positions. - Replace Seals and Piston Assembly. |

#### General Service Hints For Meter Control

Problem: Softener Delivers Hard Water.

Cause could be that . . . Reserve Capacity Has Been Exceeded.

Correction: Check salt dosage requirements and reset program wheel to provide additional reserve. Cause could be that . . . Program Wheel Is Not Rotating With Meter Output

Correction: Pull cable out of meter cover and rotate manually. Program wheel must move without binding and clutch must give positive “clicks” when program wheel strikes regeneration stop. If it does not, replace timer.

Cause could be that . . . Meter Is Not Measuring Flow. Correction: Check meter with meter checker.

## Service Position

BRINE VALVE

FLOW CONTROL

DRAIN

DRAIN

BRINE LEVEL

OUTLET

BRINE TANK

RESIN TANK

INLET

Hard water enters unit at valve inlet and flows down thru the mineral in the mineral tank. Conditioned water enters center tube thru the bottom distributor — then flows up thru the center tube — around the piston and out the side outlet of the valve.

Page 38

## Backwash Position

BRINE VALVE

FLOW CONTROL

DRAIN

INLET

BRINE LEVEL

OUTLET

BRINE TANK

RESIN TANK

Hard water enters unit at valve inlet — flows to the front passage and up through the front passage to regenerating valve — down the center tube — thru the bottom distributor and up thru the mineral — around the piston and out the drain line. If optional no hard water by pass piston is used water flow to outlet is prevented by an extended section of the service piston which closes the outlet port from by pass water until the end of rapid rinse.

## Brine Position

BRINE VALVE FLOW CONTROL

INLET

BRINE LEVEL

OUTLET

BRINE TANK

RESIN TANK

Hard water enters unit at valve inlet — flows up into injector housing and down thru nozzle and orifice to draw brine from the brine tank — brine flows down thru mineral and enters the center tube thru bottom distributor — flows up thru center tube — around the piston and out thru the drain line.

Page 40

## Slow Rinse Position

BRINE VALVE

FLOW CONTROL

DRAIN

OUTLET

BRINE LEVEL

BRINE TANK

RESIN TANK

INLET

### Page 41

Hard water enters unit at valve inlet — flows up into injector housing and down thru nozzle and orifice

— around the piston — down thru mineral — enters center tube thru bottom distributor — flows up thru center tube — around piston and out thru the drain line.

## Rapid Rinse

BRINE VALVE

FLOW CONTROL

DRAIN

INLET

OUTLET

BRINE LEVEL

BRINE TANK

RESIN TANK

Hard water flows thru the regenerating valve directly down thru the mineral into the bottom distributor and up thru the center tube — around the piston and out the drain line.

Page 42

## Brine Tank Fill Position

BRINE VALVE

FLOW CONTROL

DRAIN

INLET

INLET

OUTLET

BRINE LEVEL

BRINE TANK

RESIN TANK

Hard water flows thru the service valve and down thru the mineral. Conditioned water enters the bottom distributor — flows up the center tube around the piston to the outlet. Hard water flows to the regenerating valve thru the injector housing and brine valve to fill the brine tank.

Page 43

## Flow Data & Injector Draw Rates

2900 CPI Down Flow Valve

Backwash(BW), Service and Rapid Rinse(RR) Pressure Differential

Backwash, Service and Rapid Rinse

Pressure Differential

30

25

Pressure Differential - PSID

20

15

10

5

0

0	10	20	30	40	50	60	70	80	90	100	110	120	130	140	150

BW	Service	RR

Flow Rate - GPM

2900 CPI Treated Water Down Flow Valve

Backwash(BW), Service and Rapid Rinse(RR) Pressure Differential

2900 Treated Water Down Flow Valve Backwash, Service and Rapid Rinse Pressure Differential

30

25

Pressure Differential - PSID

20

15

10

5

0

0	20

40	60

80

Flow Rate - GPM

100

120

140

BW	Service	RR

5

4.5

4

3.5

3

2.5

2

1.5

1

0.5

0

1700 4C injector

2900 DRAW 2900 RINSE 2900 TOTAL

20	40	60	PSI      80	100	120

8

1700 5C injector

7

6

5

4

3

2

1	2900 DRAW     2900 RINSE     2900 TOTAL 0

20	40	60	PSI      80	100	120

3.5

3

2.5

2

1.5

1

0.5

0

DRAW

RINSE TOTAL

20	40

60	PSI 80

100

120

1700 3C injector

2.5

2

DRAW

RINSE TOTAL

1600 3 injector

1.5

1

0.5

0

20

40

60 PSI 80

100

120

GPM

GPM

GPM

GPM

GPM

GPM

Flow Data & Injector Draw Rates

| 8 |  |  | 1700 7C injector with 35gpm DLFC |
| --- | --- | --- | --- |
| 7 |  |  |  |
| 6 |  | 10.00 |  |
| 5 |  | 8.00 |  |
| 4 |  |  |  |

1700 5C injector

3

2

1	2900 DRAW     2900 RINSE     2900 TOTAL 0

20	40	60	PSI      80	100	120

12.00

6.00

4.00

2.00

2900 DRAW	2900 RINSE	2900 TOTAL

0.00

no DLFC draw	no DLFC rinse	no DLFC total

20

40

60	PSI 80

100

120

TR203941 41606

## Environmental Backplate Line Drawing

61500-2900LNE

## Environmental Designer

System #4 - Typical Single Tank Installation With Optional Meter

# MODEL 2900

## System #5 - Interlock - Typical Twin Tank Installation With Optional Meter Interlock And No Hard Water Bypass

### Page 49

Printed in U.S.A.

# MODEL 2900

## System #6 – Twin Series Regeneration System #7 – Twin Alternator Installation

POWER CORD

BRINE TANK

BRINE TANK

UNIT 1

INERLOCK CABLE

BRINE LINE

DRAIN LINE

REMOTE METER

MANUAL SHUTOFF VALVE

BRINE TANK

RESIN TANK

UNIT 2

Note: On System 7 power cord is on Unit 2. Note: System 7 only one Brine Tank.

## System #4-Single Valve Regeneration Immediate and Delayed Valve Wiring

18684

## System #4-With Remote Signal Start Valve Wiring

15405

System #5-Interlocked Regeneration Valve Wiring

18685-01

18685-02

System #6-Series Regeneration Valve Wiring

18686-01

18686-02

## System #7-Alternating Regeneration Valve Wiring

18687-01

18687-02

16172

System #7-Alternating Regeneration Multi-Valve System Valve Wiring

Notes

P/N 15238	Rev. E 03/05