Maintenance: Solaronics heated Blower

BEFORE performing any maintenance, disconnect and lockout the electrical supply by positive means. All maintenance must be performed by qualified service personnel.

## MONTHLY:

## During heating season, check operation of safety controls:

## Flame Safeguard/Relay – ‘FR’

## Air Flow Switch – ‘AF-1’

## High Temperature Limit – ‘HTL’

## Wipe lens of flame scanner ‘FS’ and check that viewing hole is not blocked

## Check that sensing points of air flow switch ‘AF-1’ are not blocked

## Clean inlet air guard (if installed) of any dirt/dust buildup to assure clear passageways for combustion air

## Clean propeller blades: a buildup of dirt and dust can cause an imbalance

## ANNUALLY:

## At start of heating season:

## In car washes, wipe clean the ignition wire and spark plug ‘SP’

## Check and clean burner, burner ports, and mixing plates

## Check gas manifold pressure (Refer to page 4 for proper setting)

## Replace spark plug ‘SP’, especially in car wash applications

## Check high voltage lead-in wire for deterioration

## Check and clean propeller blades · Check motor mounting

## Check burner mounting · Check heaters’ support mounting

## Check piping and controls for gas leaks NEVER USE A FLAME! – use a soap solution

## Lubricate motor according to manufacturers’ directions in accordance with some codes or under adverse conditions, such as a car wash, it may be necessary to inspect or service some items more often.

## The use of an inspection form is recommended. Preventative maintenance is the best way to get long and trouble-free service from this heater.